## Sheet1
No. | X | Y | Phase | Phase Test | P (kW) @ pf=0.95 | Q(kVar) @ pf =0.95 | I(A) | I10(A) | R | Y | B |  | R | Y | B
1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2 | 40 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
3 | 80 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
4 | 120 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
5 | 160 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
6 | 200 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
7 | 240 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
8 | 280 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
9 | 320 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
10 | 360 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
11 | 400 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
12 | 440 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
13 | 480 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
14 | 88 | 490 | 1 | 1 | 6.4736 | 2.1278 | 29.6275 | 37.0006 | 6.4736 | 0 | 0 |  | 29.6275 | 0 | 0
15 | 128 | 490 | 1 | 2 | 1.2 | 0.39442 | 5.492 | 6.8587 | 0 | 1.2 | 0 |  | 0 | 5.492 | 0
16 | 168 | 490 | 1 | 3 | 2.3 | 0.75597 | 10.5263 | 13.1459 | 0 | 0 | 2.3 |  | 0 | 0 | 10.5263
17 | 208 | 490 | 1 | 2 | 1.28 | 0.42072 | 5.8581 | 7.316 | 0 | 1.28 | 0 |  | 0 | 5.8581 | 0
18 | 248 | 490 | 1 | 3 | 1.56 | 0.51275 | 7.1396 | 8.9164 | 0 | 0 | 1.56 |  | 0 | 0 | 7.1396
19 | 288 | 490 | 1 | 2 | 2.5 | 0.82171 | 11.4416 | 14.289 | 0 | 2.5 | 0 |  | 0 | 11.4416 | 0
20 | 328 | 490 | 1 | 3 | 2.1 | 0.69024 | 9.611 | 12.0028 | 0 | 0 | 2.1 |  | 0 | 0 | 9.611
21 | 368 | 490 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
22 | 408 | 490 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
23 | 63 | 0 | 3 | 0 | 10 | 3.2868 | 15.1934 | 18.9745 | 3.3333 | 3.3333 | 3.3333 |  | 15.1934 | 15.1934 | 15.1934
24 | 87 | 0 | 3 | 0 | 15 | 4.9303 | 22.7901 | 28.4618 | 5 | 5 | 5 |  | 22.7901 | 22.7901 | 22.7901
25 | 115 | 0 | 3 | 0 | 12.5 | 4.1086 | 18.9918 | 23.7181 | 4.1667 | 4.1667 | 4.1667 |  | 18.9918 | 18.9918 | 18.9918
26 | 145 | 0 | 3 | 0 | 8 | 2.6295 | 12.1547 | 15.1796 | 2.6667 | 2.6667 | 2.6667 |  | 12.1547 | 12.1547 | 12.1547
27 | 176 | 0 | 3 | 0 | 9.5 | 3.1225 | 14.4338 | 18.0258 | 3.1667 | 3.1667 | 3.1667 |  | 14.4338 | 14.4338 | 14.4338
28 | 105 | 0 | 3 | 0 | 8.75 | 2.876 | 13.2942 | 16.6027 | 2.9167 | 2.9167 | 2.9167 |  | 13.2942 | 13.2942 | 13.2942
29 | 153 | 0 | 3 | 0 | 10 | 3.2868 | 15.1934 | 18.9745 | 3.3333 | 3.3333 | 3.3333 |  | 15.1934 | 15.1934 | 15.1934
30 | 38 | 196 | 3 | 0 | 12 | 3.9442 | 18.2321 | 22.7694 | 4 | 4 | 4 |  | 18.2321 | 18.2321 | 18.2321
31 | 124 | 175 | 3 | 0 | 13.5 | 4.4372 | 20.5111 | 25.6156 | 4.5 | 4.5 | 4.5 |  | 20.5111 | 20.5111 | 20.5111
32 | 39 | 221 | 3 | 0 | 12 | 3.9442 | 18.2321 | 22.7694 | 4 | 4 | 4 |  | 18.2321 | 18.2321 | 18.2321
33 | 41 | 236 | 3 | 0 | 7.5 | 2.4651 | 11.3951 | 14.2309 | 2.5 | 2.5 | 2.5 |  | 11.3951 | 11.3951 | 11.3951
34 | 69 | 229 | 3 | 0 | 9.8 | 3.2211 | 14.8896 | 18.595 | 3.2667 | 3.2667 | 3.2667 |  | 14.8896 | 14.8896 | 14.8896
35 | 111 | 217 | 3 | 0 | 11.2 | 3.6813 | 17.0166 | 21.2515 | 3.7333 | 3.7333 | 3.7333 |  | 17.0166 | 17.0166 | 17.0166
36 | 43 | 254 | 3 | 0 | 11.8 | 3.8785 | 17.9282 | 22.3899 | 3.9333 | 3.9333 | 3.9333 |  | 17.9282 | 17.9282 | 17.9282
37 | 66 | 260 | 3 | 0 | 14 | 4.6016 | 21.2708 | 26.5643 | 4.6667 | 4.6667 | 4.6667 |  | 21.2708 | 21.2708 | 21.2708
38 | 46 | 274 | 3 | 0 | 18 | 5.9163 | 27.3482 | 34.1541 | 6 | 6 | 6 |  | 27.3482 | 27.3482 | 27.3482
39 | 46 | 291 | 3 | 0 | 17.89 | 5.8802 | 27.181 | 33.9454 | 5.9633 | 5.9633 | 5.9633 |  | 27.181 | 27.181 | 27.181
40 | 48 | 306 | 3 | 0 | 8.7 | 2.8596 | 13.2183 | 16.5078 | 2.9 | 2.9 | 2.9 |  | 13.2183 | 13.2183 | 13.2183
41 | 50 | 373 | 3 | 0 | 9.8 | 3.2211 | 14.8896 | 18.595 | 3.2667 | 3.2667 | 3.2667 |  | 14.8896 | 14.8896 | 14.8896
42 | 65 | 362 | 3 | 0 | 11.87 | 3.9015 | 18.0346 | 22.5227 | 3.9567 | 3.9567 | 3.9567 |  | 18.0346 | 18.0346 | 18.0346
43 | 66 | 371 | 3 | 0 | 21.3 | 7.001 | 32.362 | 40.4157 | 7.1 | 7.1 | 7.1 |  | 32.362 | 32.362 | 32.362
44 | 68 | 382 | 3 | 0 | 22.5 | 7.3954 | 34.1852 | 42.6926 | 7.5 | 7.5 | 7.5 |  | 34.1852 | 34.1852 | 34.1852
45 | 100 | 365 | 1 | 2 | 1.3 | 0.42729 | 5.9497 | 7.4303 | 0 | 1.3 | 0 |  | 0 | 5.9497 | 0
46 | 66 | 419 | 1 | 3 | 1.9 | 0.6245 | 8.6957 | 10.8597 | 0 | 0 | 1.9 |  | 0 | 0 | 8.6957
47 | 59 | 459 | 1 | 2 | 2.4 | 0.78884 | 10.984 | 13.7175 | 0 | 2.4 | 0 |  | 0 | 10.984 | 0
48 | 59 | 482 | 1 | 1 | 1.1 | 0.36155 | 5.0343 | 6.2872 | 1.1 | 0 | 0 |  | 5.0343 | 0 | 0
49 | 103 | 463 | 1 | 1 | 1.2 | 0.39442 | 5.492 | 6.8587 | 1.2 | 0 | 0 |  | 5.492 | 0 | 0
50 | 121 | 460 | 1 | 3 | 1.3 | 0.42729 | 5.9497 | 7.4303 | 0 | 0 | 1.3 |  | 0 | 0 | 5.9497
51 | 134 | 464 | 1 | 2 | 1.5 | 0.49303 | 6.865 | 8.5734 | 0 | 1.5 | 0 |  | 0 | 6.865 | 0
52 | 137 | 419 | 1 | 1 | 1.8 | 0.59163 | 8.238 | 10.2881 | 1.8 | 0 | 0 |  | 8.238 | 0 | 0
53 | 151 | 411 | 1 | 3 | 2.3 | 0.75597 | 10.5263 | 13.1459 | 0 | 0 | 2.3 |  | 0 | 0 | 10.5263
54 | 164 | 419 | 1 | 2 | 1.7 | 0.55876 | 7.7803 | 9.7166 | 0 | 1.7 | 0 |  | 0 | 7.7803 | 0
55 | 182 | 471 | 3 | 0 | 2.5 | 0.82171 | 3.7984 | 4.7436 | 0.83333 | 0.83333 | 0.83333 |  | 3.7984 | 3.7984 | 3.7984
56 | 177 | 461 | 1 | 1 | 3.2 | 1.0518 | 14.6453 | 18.29 | 3.2 | 0 | 0 |  | 14.6453 | 0 | 0
57 | 185 | 426 | 1 | 3 | 1.3 | 0.42729 | 5.9497 | 7.4303 | 0 | 0 | 1.3 |  | 0 | 0 | 5.9497
58 | 185 | 418 | 1 | 2 | 1.5 | 0.49303 | 6.865 | 8.5734 | 0 | 1.5 | 0 |  | 0 | 6.865 | 0
59 | 196 | 412 | 1 | 3 | 1.2 | 0.39442 | 5.492 | 6.8587 | 0 | 0 | 1.2 |  | 0 | 0 | 5.492
60 | 220 | 406 | 1 | 2 | 1.1 | 0.36155 | 5.0343 | 6.2872 | 0 | 1.1 | 0 |  | 0 | 5.0343 | 0
61 | 239 | 467 | 1 | 1 | 0.9 | 0.29582 | 4.119 | 5.1441 | 0.9 | 0 | 0 |  | 4.119 | 0 | 0
62 | 267 | 399 | 1 | 3 | 0.464 | 0.15251 | 2.1236 | 2.652 | 0 | 0 | 0.464 |  | 0 | 0 | 2.1236
63 | 354 | 469 | 1 | 3 | 0.411 | 0.13509 | 1.881 | 2.3491 | 0 | 0 | 0.411 |  | 0 | 0 | 1.881
64 | 372 | 472 | 1 | 2 | 0.434 | 0.14265 | 1.9863 | 2.4806 | 0 | 0.434 | 0 |  | 0 | 1.9863 | 0
65 | 423 | 473 | 1 | 1 | 0.437 | 0.14363 | 2 | 2.4977 | 0.437 | 0 | 0 |  | 2 | 0 | 0
66 | -61 | 24 | 1 | 3 | 0.292 | 0.095976 | 1.3364 | 1.669 | 0 | 0 | 0.292 |  | 0 | 0 | 1.3364
67 | -27 | 32 | 1 | 2 | 0.369 | 0.12128 | 1.6888 | 2.1091 | 0 | 0.369 | 0 |  | 0 | 1.6888 | 0
68 | -12 | 38 | 1 | 1 | 0.445 | 0.14626 | 2.0366 | 2.5435 | 0.445 | 0 | 0 |  | 2.0366 | 0 | 0
69 | -3 | 38 | 1 | 3 | 0.446 | 0.14659 | 2.0412 | 2.5492 | 0 | 0 | 0.446 |  | 0 | 0 | 2.0412
70 | -12 | 50 | 1 | 2 | 0.381 | 0.12523 | 1.7437 | 2.1777 | 0 | 0.381 | 0 |  | 0 | 1.7437 | 0
71 | -10 | 57 | 1 | 1 | 0.333 | 0.10945 | 1.524 | 1.9033 | 0.333 | 0 | 0 |  | 1.524 | 0 | 0
72 | -9 | 63 | 1 | 3 | 0.371 | 0.12194 | 1.6979 | 2.1205 | 0 | 0 | 0.371 |  | 0 | 0 | 1.6979
73 | -17 | 72 | 1 | 2 | 0.435 | 0.14298 | 1.9908 | 2.4863 | 0 | 0.435 | 0 |  | 0 | 1.9908 | 0
74 | -16 | 89 | 1 | 1 | 0.414 | 0.13608 | 1.8947 | 2.3663 | 0.414 | 0 | 0 |  | 1.8947 | 0 | 0
75 | -4 | 104 | 1 | 3 | 0.423 | 0.13903 | 1.9359 | 2.4177 | 0 | 0 | 0.423 |  | 0 | 0 | 1.9359
76 | -10 | 128 | 1 | 2 | 0.332 | 0.10912 | 1.5195 | 1.8976 | 0 | 0.332 | 0 |  | 0 | 1.5195 | 0
77 | -34 | 158 | 1 | 1 | 0.477 | 0.15678 | 2.1831 | 2.7264 | 0.477 | 0 | 0 |  | 2.1831 | 0 | 0
78 | -69 | 165 | 1 | 3 | 0.412 | 0.13542 | 1.8856 | 2.3548 | 0 | 0 | 0.412 |  | 0 | 0 | 1.8856
79 | -84 | 166 | 1 | 2 | 0.336 | 0.11044 | 1.5378 | 1.9204 | 0 | 0.336 | 0 |  | 0 | 1.5378 | 0
80 | -102 | 164 | 1 | 2 | 0.361 | 0.11865 | 1.6522 | 2.0633 | 0 | 0.361 | 0 |  | 0 | 1.6522 | 0
81 | -6 | 165 | 1 | 3 | 0.382 | 0.12556 | 1.7483 | 2.1834 | 0 | 0 | 0.382 |  | 0 | 0 | 1.7483
82 | -4 | 178 | 1 | 1 | 0.332 | 0.10912 | 1.5195 | 1.8976 | 0.332 | 0 | 0 |  | 1.5195 | 0 | 0
83 | 5 | 205 | 1 | 1 | 0.347 | 0.11405 | 1.5881 | 1.9833 | 0.347 | 0 | 0 |  | 1.5881 | 0 | 0
84 | 3 | 230 | 1 | 2 | 0.454 | 0.14922 | 2.0778 | 2.5949 | 0 | 0.454 | 0 |  | 0 | 2.0778 | 0
85 | 8 | 247 | 1 | 3 | 0.451 | 0.14824 | 2.0641 | 2.5777 | 0 | 0 | 0.451 |  | 0 | 0 | 2.0641
86 | 7 | 289 | 1 | 1 | 0.469 | 0.15415 | 2.1465 | 2.6806 | 0.469 | 0 | 0 |  | 2.1465 | 0 | 0
87 | 13 | 322 | 1 | 2 | 0.372 | 0.12227 | 1.7025 | 2.1262 | 0 | 0.372 | 0 |  | 0 | 1.7025 | 0
88 | 0 | 320 | 1 | 3 | 0.389 | 0.12786 | 1.7803 | 2.2234 | 0 | 0 | 0.389 |  | 0 | 0 | 1.7803
89 | 11 | 337 | 1 | 1 | 0.494 | 0.16237 | 2.2609 | 2.8235 | 0.494 | 0 | 0 |  | 2.2609 | 0 | 0
90 | 13 | 349 | 1 | 2 | 0.357 | 0.11734 | 1.6339 | 2.0405 | 0 | 0.357 | 0 |  | 0 | 1.6339 | 0
91 | 21 | 419 | 1 | 3 | 0.426 | 0.14002 | 1.9497 | 2.4349 | 0 | 0 | 0.426 |  | 0 | 0 | 1.9497
92 | 20 | 428 | 1 | 2 | 0.359 | 0.118 | 1.643 | 2.0519 | 0 | 0.359 | 0 |  | 0 | 1.643 | 0
93 | -77 | 413 | 1 | 1 | 0.439 | 0.14429 | 2.0092 | 2.5092 | 0.439 | 0 | 0 |  | 2.0092 | 0 | 0
94 | -17 | 514 | 1 | 3 | 0.358 | 0.11767 | 1.6384 | 2.0462 | 0 | 0 | 0.358 |  | 0 | 0 | 1.6384
95 | 42 | 495 | 1 | 2 | 0.58 | 0.19064 | 2.6545 | 3.3151 | 0 | 0.58 | 0 |  | 0 | 2.6545 | 0
96 | -14 | 527 | 1 | 3 | 1.8 | 0.59163 | 8.238 | 10.2881 | 0 | 0 | 1.8 |  | 0 | 0 | 8.238
97 | -15 | 540 | 1 | 1 | 2.8 | 0.92032 | 12.8146 | 16.0037 | 2.8 | 0 | 0 |  | 12.8146 | 0 | 0
98 | 31 | 504 | 1 | 2 | 0.58 | 0.19064 | 2.6545 | 3.3151 | 0 | 0.58 | 0 |  | 0 | 2.6545 | 0
99 | 33 | 516 | 1 | 2 | 0.424 | 0.13936 | 1.9405 | 2.4234 | 0 | 0.424 | 0 |  | 0 | 1.9405 | 0
100 | -8 | 500 | 1 | 2 | 0.365 | 0.11997 | 1.6705 | 2.0862 | 0 | 0.365 | 0 |  | 0 | 1.6705 | 0
101 | 33 | 566 | 1 | 3 | 0.435 | 0.14298 | 1.9908 | 2.4863 | 0 | 0 | 0.435 |  | 0 | 0 | 1.9908
102 | 40 | 629 | 1 | 2 | 0.357 | 0.11734 | 1.6339 | 2.0405 | 0 | 0.357 | 0 |  | 0 | 1.6339 | 0
103 | 52 | 619 | 1 | 2 | 0.304 | 0.09992 | 1.3913 | 1.7375 | 0 | 0.304 | 0 |  | 0 | 1.3913 | 0
104 | 51 | 680 | 1 | 3 | 0.465 | 0.15284 | 2.1281 | 2.6578 | 0 | 0 | 0.465 |  | 0 | 0 | 2.1281
105 | 51 | 691 | 1 | 2 | 0.43 | 0.14133 | 1.968 | 2.4577 | 0 | 0.43 | 0 |  | 0 | 1.968 | 0
106 | 69 | 599 | 1 | 3 | 0.369 | 0.12128 | 1.6888 | 2.1091 | 0 | 0 | 0.369 |  | 0 | 0 | 1.6888
107 | 82 | 638 | 1 | 1 | 0.437 | 0.14363 | 2 | 2.4977 | 0.437 | 0 | 0 |  | 2 | 0 | 0
108 | 65 | 508 | 1 | 2 | 0.428 | 0.14068 | 1.9588 | 2.4463 | 0 | 0.428 | 0 |  | 0 | 1.9588 | 0
109 | 72 | 537 | 1 | 3 | 0.364 | 0.11964 | 1.6659 | 2.0805 | 0 | 0 | 0.364 |  | 0 | 0 | 1.6659
110 | 75 | 549 | 1 | 1 | 0.358 | 0.11767 | 1.6384 | 2.0462 | 0.358 | 0 | 0 |  | 1.6384 | 0 | 0
111 | 74 | 563 | 1 | 2 | 0.501 | 0.16467 | 2.2929 | 2.8635 | 0 | 0.501 | 0 |  | 0 | 2.2929 | 0
112 | 38 | 581 | 1 | 3 | 0.313 | 0.10288 | 1.4325 | 1.789 | 0 | 0 | 0.313 |  | 0 | 0 | 1.4325
113 | 106 | 506 | 1 | 1 | 0.435 | 0.14298 | 1.9908 | 2.4863 | 0.435 | 0 | 0 |  | 1.9908 | 0 | 0
114 | 119 | 506 | 1 | 3 | 0.389 | 0.12786 | 1.7803 | 2.2234 | 0 | 0 | 0.389 |  | 0 | 0 | 1.7803
115 | 132 | 490 | 1 | 2 | 0.389 | 0.12786 | 1.7803 | 2.2234 | 0 | 0.389 | 0 |  | 0 | 1.7803 | 0
116 | 158 | 512 | 1 | 1 | 0.382 | 0.12556 | 1.7483 | 2.1834 | 0.382 | 0 | 0 |  | 1.7483 | 0 | 0
117 | 178 | 511 | 1 | 3 | 0.342 | 0.11241 | 1.5652 | 1.9547 | 0 | 0 | 0.342 |  | 0 | 0 | 1.5652
118 | 189 | 512 | 1 | 2 | 1.5 | 0.49303 | 6.865 | 8.5734 | 0 | 1.5 | 0 |  | 0 | 6.865 | 0
119 | 180 | 570 | 1 | 3 | 2.34 | 0.76912 | 10.7094 | 13.3746 | 0 | 0 | 2.34 |  | 0 | 0 | 10.7094
120 | 259 | 513 | 1 | 1 | 0.415 | 0.1364 | 1.8993 | 2.372 | 0.415 | 0 | 0 |  | 1.8993 | 0 | 0
121 | 269 | 512 | 1 | 1 | 3.3 | 1.0847 | 15.103 | 18.8615 | 3.3 | 0 | 0 |  | 15.103 | 0 | 0
122 | 275 | 522 | 1 | 2 | 2.2 | 0.72311 | 10.0686 | 12.5744 | 0 | 2.2 | 0 |  | 0 | 10.0686 | 0
123 | 284 | 522 | 1 | 3 | 0.357 | 0.11734 | 1.6339 | 2.0405 | 0 | 0 | 0.357 |  | 0 | 0 | 1.6339
124 | 293 | 511 | 1 | 3 | 1.2 | 0.39442 | 5.492 | 6.8587 | 0 | 0 | 1.2 |  | 0 | 0 | 5.492
125 | 350 | 507 | 1 | 2 | 0.473 | 0.15547 | 2.1648 | 2.7035 | 0 | 0.473 | 0 |  | 0 | 2.1648 | 0
126 | 357 | 507 | 1 | 1 | 0.392 | 0.12884 | 1.7941 | 2.2405 | 0.392 | 0 | 0 |  | 1.7941 | 0 | 0
127 | 373 | 505 | 1 | 3 | 0.426 | 0.14002 | 1.9497 | 2.4349 | 0 | 0 | 0.426 |  | 0 | 0 | 1.9497
128 | 409 | 500 | 1 | 2 | 0.416 | 0.13673 | 1.9039 | 2.3777 | 0 | 0.416 | 0 |  | 0 | 1.9039 | 0
129 | 422 | 500 | 1 | 1 | 0.349 | 0.11471 | 1.5973 | 1.9948 | 0.349 | 0 | 0 |  | 1.5973 | 0 | 0 | Limit_UC | 1.1
Total P (kW) | [5 empty] | 361.0406 |  |  | 120.4319 | 120.3203 | 120.2883 |  | 549.4488 | 548.938 | 548.7916 | UC | 1
Total Q (kVar) | [5 empty] | 118.6683 | [5 empty] | 0.5 |  |  |  | I_avg | 549.0595
Total S (kVA) | [5 empty] | 380.0427 | [5 empty] | 120.3469
Phase Number | [5 empty] | 3 |  |  | Arrangement Phase Division Completed !! |  |  |  | Arrangement Phase Division Completed !!
Total Demand Current (A) | [5 empty] | 577.4152
Total P (kW) for 10 years | [5 empty] | 462.1625 | [10 empty] | 0.38932
[8 empty] | Current | 551.1759 | 550.6651 | 550.5187 |  | 120 kW | 120 kW | 120 kW |  | 0.070907
[5 empty] | P_demand for 10 years | 462.1625
[5 empty] | Q_demand for 10 years | 151.9055
[5 empty] | S_demand for 10 years | 486.4868
[5 empty] | S_Transformer | 583.7842

## Load Estimation
Subject: |  | LOAD ESTIMATION FOR HOUSEHOLD
Date: |  | 2025-07-26
Item |  | Description | Phase | Unit | Qty | Unit Power (W) | Ku | Demand Power (W) | Sub Total Power (W) | Ks | Demand Power (W) | Current (A) | Load Division |  |  | Phase Test |  |  | Phase Test |  |  | Preliminary Phase division |  |  | Q (W) | Cable
[13 empty] | R | Y | B | R | Y | B | R | B | Y | R | B | Y
Household Location (X=88, Y=490)
DISTRIBUTION BOARD
A | 2 | LIGHTING SYSTEM
1 |  | DB-L01 | 1 | [5 empty] | 200 | 1 | 200 | 1.1364 | 200 | 0 | 0 | 200 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 150 | 2.5 mm²
|  | - LED PANEL LIGHT 1.2m X 0.3m |  | pcs | 2 | 40 | 1 | 80
|  | - LED PANEL LIGHT 0.6m X 0.6m |  | pcs | 3 | 40 | 1 | 120
1 |  | DB-L02 | 1 | [5 empty] | 156 | 1 | 156 | 0.88636 | 156 | 0 | 0 | 156 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 117 | 2.5 mm131
|  | - LED DOWN LIGH 1 X 12W |  | pcs | 3 | 12 | 1 | 36
|  | - BATTEN LUMINAIRE 2 X 20W |  | pcs | 3 | 40 | 1 | 120
1 |  | DB-L03 | 1 | [5 empty] | 60 | 1 | 60 | 0.34091 | 60 | 0 | 0 | 60 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 45 | 2.5 mm132
|  | - BATTEN LUMINAIRE 1 X 20W |  | pcs | 3 | 20 | 1 | 60
B | 2 | POWER SOCKET OUTLET SYSTEM
1 |  | DB-S01 | 1 | [5 empty] | 1800 | 0.8 | 1440 | 8.1818 | 1440 | 0 | 0 | 1440 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 1350
|  | - DOUBLE POWER SOCKET OUTLET |  | pcs | 4 | 300 | 1 | 1200
|  | - SINGLE POWER SOCKET OUTLET |  | pcs | 4 | 150 | 1 | 600
1 |  | DB-S02 | 1 | [5 empty] | 750 | 0.8 | 600 | 3.4091 | 600 | 0 | 0 | 600 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 562.5
|  | - SINGLE POWER SOCKET OUTLET |  | pcs | 5 | 150 | 1 | 750
1 |  | DB-S03 | 1 | [5 empty] | 1050 | 0.8 | 840 | 4.7727 | 840 | 0 | 0 | 840 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 787.5
|  | - SINGLE POWER SOCKET OUTLET |  | pcs | 7 | 150 | 1 | 1050
C | 2 | AIR CONDITIONING
1 |  | DB-AC01 | 1 | [5 empty] | 1440 | 1 | 1440 | 8.1818 | 1440 | 0 | 0 | 1440 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 1080
|  | - AIR CONDITIONING |  | pcs | 1 | 1800 | 0.8 | 1440
1 |  | DB-AC02 | 1 | [5 empty] | 1440 | 1 | 1440 | 8.1818 | 1440 | 0 | 0 | 1440 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 1080
|  | - AIR CONDITIONING |  | pcs | 1 | 1800 | 0.8 | 1440
1 |  | DB-AC03 | 1 | [5 empty] | 1440 | 1 | 1440 | 8.1818 | 1440 | 0 | 0 | 1440 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 1080
|  | - AIR CONDITIONING |  | pcs | 1 | 1800 | 0.8 | 1440
SUB TOAL DEMAND LOAD (W) | [10 empty] | 7616 | 36.0165 | 7616 | 0 | 0
DIVERSIFY FACTOR (Ks) | [10 empty] | 0.85 |  | Re-arange load againt!
TOTAL DEMAND LOAD (W) | [10 empty] | 6473.6
PHASE NUMBER | [10 empty] | 1
POWER FACTOR (COS φ) | [10 empty] | 0.817
APPARENT POWER (VA) | [10 empty] | 7921
[11 empty] | Tolerence by Phase |  | 5077.3333 | -2538.6667 | -2538.6667
[9 empty] | Allowable Tolerence |  |  |  | 500 | W
[9 empty] | Load average for each phase |  |  |  | 2538.6667 | W

## Feeder01
N. | Coordinates |  | Phase | P [kW] | Q [kVar]
| X | Y
1 | 137 | 419 | 1 | 1.8 | 0.59
2 | 151 | 411 | 1 | 2.3 | 0.76
3 | 164 | 419 | 1 | 1.7 | 0.56
4 | 164 | 426 | 1 | 1.3 | 0.43
5 | 164 | 418 | 1 | 1.5 | 0.49
6 | 164 | 412 | 1 | 1.2 | 0.39
7 | 164 | 406 | 1 | 1.1 | 0.36
8 | 164 | 399 | 1 | 0.464 | 0.15
|  | initial year |  | 11.364 | 3.73
|  | in 10 years |  | 14.5469 | 4.7747
|  | demand current |  | 22.1017
|  | maximum current |  | 23.0226